## Slide 1: COMPLIANCE VIOLATIONS FOUND DURING INSPECTIONS
Office of Land Resources
Regulated Storage Tanks

## Slide 2: Randy Beard District 10 Inspector Fort Smith Field Office

## Slide 3: Release Prevention
Spill Prevention
Overfill Prevention
Corrosion Protection

## Slide 4: Spill Prevention
Keep spill buckets free of any liquid or debris
Repair or replace spill bucket when damaged

## Slide 5: Spill bucket with liquid

## Slide 6: Crack in spill bucket

## Slide 7: Crack in spill bucket

## Slide 8: Product found in monitoring well

## Slide 9: Overfill Prevention
Do not remove automatic shut-off except when testing or replacing
Maintain device as operable

## Slide 10: Drop tube out of tank

## Slide 11: Corrosion Protection
Current three-year corrosion protection system recertification for tanks and/or piping
For flex lines, if needed
For subpump, if needed
Sixty-day rectifier check for impressed current system

## Slide 12: Without protection, liquid in sump will cause corrosion to metal components

## Slide 13: Corrosion on turbine pump

## Slide 14: Rectifier reading zero amps

## Slide 15: John Lamb District 5 Inspector El Dorado Field Office

## Slide 16: Release Detection Tanks and Piping
Monthly monitoring results documentation
Monthly ATG results
Records for the two most recent consecutive months
Records for eight of the last 12 months
(new regulations now require 10 of the last 12
months)

## Slide 17: Release Detection Tanks and Piping
Annually check function of line leak detectors
Annual line tightness test documentation
Monthly interstitial monitoring records

## Slide 18: Line leak detector test

## Slide 19: Line tightness test

## Slide 20: Dispenser sump with interstitial monitoring

## Slide 21: Interstitial monitoring for double-walled piping

## Slide 22: Interstitial monitoring results

## Slide 23: Registration Requirements
New underground storage tanks prior to fuel delivery
Change in ownership

## Slide 24: Operator Training
Trained Class C operators on all shifts
Class C operator training documented on required ADEQ forms

## Slide 25
Questions